Electrical Wiring

A network of wires connecting various accessories for distribution of electrical energy from the supplier meter board to the different electrical energy consuming devices such as lamps, fans& other domestic appliances through controlling and safety devices is known as a wiring system.

The supplier (electricity department) service cable feeding electricity to energy meter and after that terminates at service fuse, which is also called service cut-out. Up to service cut-out, it is the property of supplier. The onwards wiring from service cut-out is called consumer’s terminal, such cables are entirely under the control of consumer. A typical house wiring circuit is shown below:

Distribution of Electrical Energy:

As per recommendation of Indian Standards (IS) the maximum number of points of lights, fans & 5 A sockets that can be connected in one circuit is 10 and maximum load that can be connected in such a circuit is 800 watts. In case more load or points, more than one circuit is required.

(i) Distribution Board System: In distribution board system, which is most commonly adopted for distribution of electrical energy in a building, the fuse of various circuits are grouped together on a distribution board, sometimes also known as Fuse Board. Connection is shown in fig below-

Two copper strips known as bus-bar, fixed in a distribution board of hard wood or metal case are connected to the supply mains through a linked switch (may bes operated by a handle connected outside the box) so that the installation can be switched off as a hole from both poles of the supply, if required.

In distribution board shown above has 4 ways for four circuits but there is no limit to the number of ways or circuits provided the cable feeding the board is large enough to carry the total load current.

In large buildings, however, if one distribution board were used, some of the points would be at a considerable distance from it and in such cases it is advisable to employ sub-distribution boards either to save cable or to prevent too great voltage drop at the more distant points (lamps, fans or other appliances). The number of circuit and sub-circuits is decided as per number of points to be wired and load to be connected to the supply system.

(ii) Tree System:

This system was used in early days, now a day it is not in practice. In this system smaller branches are taken from the main branch as shown in figure and the wiring system resembles a tree. As each branch is taken off, a fuse is inserted.

Drawbacks of tree system are:-

(a) The voltage across all the lamps doesn’t remain the same. The lamp in the last branch will have least voltage across them.

(b) A number of joints are involved in every circuit.

(c) Fuses are scattered.

(d) In case of occurrence of fault all the joints have to be located, causing lot of difficulties.

Methods of Wiring:

There are two methods of wiring-

(i) Joint Box or T System: In this method of wiring, connections to appliances are made through joints. These joints are made in joint boxes by means of suitable connectors or joints cut-outs. This method of wiring doesn’t consume too much cables size.

Since this method of wiring doesn’t require too much cable it is therefore cheaper. But the money saved from buying cables will be used in buying joint boxes, thus equation is almost balanced. Now a days this method is suitable for temporary installations.

(ii) Loop-in System: This method of wiring is universally adopted. Lamps and other appliances are connected in parallel so that each appliance can be controlled individually. When a connection is required at a light or switch, the feed conductor is looped in by bringing it directly to the terminal and then carrying it forward again to the next point to be fed.

The switch and light feeds are carried round the circuit in a series of loops from one point to another until the last on the circuit is reached. The phase or line conductors are looped either in switchboard or box and neutrals are looped either in switchboard or from light or fan. Line or phase should never be looped from light or fan.

Advantages of Loop-In Method of Wiring

- It doesn’t require joint boxes and so money is saved

- In loop – in systems, no joint is concealed beneath floors or in roof spaces.

- Fault location is made easy as the points are made only at outlets so that they are accessible.

Disadvantages of Loop-In Method of Wiring

- Length of wire or cables required is more and voltage drop and copper losses are therefore more

- Looping – in switches and lamp holders is usually difficult.

System of Wiring:

The types of internal wiring usually used are

1. Cleat wiring

2. Wooden casing and capping wiring

3. CTS or TRS or PVC sheath wiring (Batten Wiring)

4. Lead sheathed or metal sheathed wiring

5. Conduit wiring

1. Cleat Wiring- This system of wiring comprises of ordinary VIR (Vulcanized Indian Rubber) or PVC (Polyvinyl Chloride) insulated wires (occasionally, sheathed and weather proof cable).

The cables are held by porcelain cleats about 6 mm above the walls or ceiling. The cleats are made in two halves, one base and other cap. The base is grooved to accommodate the cables and the cap is put over it and whole of it is screwed on wooden plugs (gutties). The screws used are of size 38 mm. The cross section of wooden gutties is 38 mm x 38 mm at big end, 25 mm x 25 mm at small end and length is about 6.5 cm.

This type of wiring is not in use in present days. Cleat wiring system is a temporary wiring system therefore it is not suitable for domestic premises.

#### Advantages of Cleat Wiring:

- It is simple and cheap wiring system

- Most suitable for temporary use i.e. under construction building or army camping

- As the cables and wires of cleat wiring system is in open air, Therefore fault in cables can be seen and repair easily.

- Cleat wiring system installation is easy and simple.

- Customization can be easily done in this wiring system e.g. alteration and addition.

- Inspection is easy and simple.

#### Disadvantages of Cleat Wiring:

- Appearance is not so good.

- Cleat wiring can’t be use for permanent use because sag may occur after sometime of the usage.

- In this wiring system, the cables and wiring is in open air, therefore, oil, steam, humidity, smoke, rain, chemical and acidic effect may damage the cables and wires.

- It is not lasting wire system because of the weather effect, risk of fire and wear & tear.

- It can be only used on 250/440 volts on low temperature.

- There is always a risk of fire and electric shock.

- It can’t be used in important and sensitive location and places.

- It is not lasting, reliable and sustainable wiring system.

#### Field of Applications: The wiring of this type is very suitable for temporary installation in dry places. This is also used where appearance is not so important and cost is the main consideration. Not suitable for use in domestic premises.

#### 2. Wooden Casing & Capping Wiring- Casing and Capping wiring system was famous wiring system in the past but, it is considered obsolete this days because of Conduit and sheathed wiring system. The cables used in this kind of wiring were either VIR or PVC or any other approved insulated cables.

#### The cables were carried through the wooden casing enclosures. The casing is made up of a strip of wood with parallel grooves cut length wise so as to accommodate VIR cables. The grooves were made to separate opposite polarity. The capping (also made of wood) used to cover the wires and cables installed and fitted in the casing.

#### Advantages of Casing Capping Wiring:

- It is cheap wiring system as compared to sheath and conduit wiring systems.

- It is strong and long-lasting wiring system.

- Customization can be easily done in this wiring system.

- If Phase and Neutral wire is installed in separate slots, then repairing is easy.

- Stay for long time in the field due to strong insulation of capping and casing.

- It stays safe from oil, Steam & smoke.

- No risk of electric shock due to covered wires and cables in casing & capping.

#### Disadvantages Casing Capping Wiring:

- There is a high risk of fire in wooden casing & capping wiring system.

- Not suitable in the acidic, alkalise and humidity conditions.

- Costly repairing and need more material.

- Material can’t be found easily in the contemporary.

- White ants may damage the casing & capping of wood.

Field of Applications: The type of wiring is suitable for low voltage domestic installations in dry places and where there is no risk of fire hazard.

3. CTS or TRS or PVC sheath Wiring (Batten Wiring)- Single core or double core or three core TRS (Tough Rubber Sheet) cables with a circular oval shape cables are used in this kind of wiring. Mostly, single core cables are preferred.

TRS cables are chemical proof, water proof, steam proof, but are slightly affected by lubricating oil. The TRS cables are run on well seasoned and straight teak wood batten with at least a thickness of 10mm.

The cables are held on the wooden batten by means of tinned brass link clips (buckle clip) already fixed on the batten with brass pins and spaced at an interval of 10cm for horizontal runs and 15cm for vertical runs.

Field of Applications: The type of wiring is suitable for low voltage installations & is extensively used for lighting purpose, mostly in domestic, commercial or industrial buildings except workshop where it is liable to mechanical injury. It can be used in damp places.

Advantages of Batten Wiring

- Wiring installation is simple and easy.

- Cheap as compared to other electrical wiring systems.

- Paraphrase is good and beautiful.

- Repairing is easy.

- Strong and long-lasting.

- Customization can be easily done in this wiring system.

- Less chance of leakage current in batten wiring system.

Disadvantages of Batten Wiring

- Can’t be installed in the humidity, Chemical effects, open and outdoor areas.

- High risk of fires.

- Not safe from external wear & tear and weather effects because, the wires are openly visible to heat, dust, steam and smoke.

- Heavy wires can’t be used in batten wiring system.

- Only suitable below 250V.

- Need more cables and wires.

4. Lead Sheathed Wiring or Metal Sheathed Wiring:

This type of wiring employs conductors that are insulated with VIR and covered with an outer sheath of lead aluminium alloy containing about 95% of lead. The metal sheath gives protection to cables from mechanical damage, moisture and atmospheric corrosion.

The whole lead covering is made electrically continuous and is connected to earth at the point of entry to protect against electrolytic action due to leaking current and to provide safety in case the sheath becomes alive. The cables are run on wooden batten and fixed by means of link clips just as in TRS wiring.

Advantages of Lead Sheathed Wiring:

- Provides protection against mechanical injuries.

- Easy to fix & looks nice because can be painted to suit building colour.

- Its life is long if proper earth continuity is maintained throughout.

- Can be used in damped situation also.

Disadvantages of Lead Sheathed Wiring:

- It is costlier than TRS wiring.

- Not suitable for places where chemical corrosion may occur.

- Skilled labour & proper supervision is required.

- In case of damage of insulation, the metal sheath becomes alive and gives shock. So, to avoid this it is necessary to provide earthing.

Field of Applications: The type of wiring is suitable for low voltage installations (up to 250V). It may be used in places exposed to sun & rains provided no joint of any kind is exposed. It may also be used in damped places. The most common application of this system is for laying sub-mains from pole or bracket to the electric meter laid by the supplier.

5. Conduit Wiring:  In this system steel tubes or PVC pipes known as conduits, as installed on the surface of walls by means of saddles or pipe hooks or buried under plaster and VIR or PVC cables are drawn afterwards by means of a GI wire of size of about 18 SWG. In order to facilitate drawing of wires number of inspection fittings is provided along its length. The conduit should be electrically & mechanically continuous & connected to earth at some suitable points. There are two types of conduit wiring according to pipe installation-

(a) Surface Conduit Wiring: If conduits installed on roof or wall, it is known as surface conduit wiring. In this wiring method, they make holes on the surface of wall on equal distances and conduit is installed.

(b) Concealed Conduit wiring: If the conduits are hidden inside the wall slots with the help of plastering, it is called concealed conduit wiring. In other words, the electrical wiring system inside wall, roof or floor with the help of plastic or metallic piping is called concealed conduit wiring. Obliviously, it is the most popular, beautiful, stronger and common electrical wiring system nowadays.

In Conduit wiring system, the conduits should be electrically continuous and connected to earth at some suitable points in case of steel conduit. Conduit wiring is a professional way of wiring a building. Mostly PVC conduits are used in domestic wiring.

The conduit protects the cables from being damaged by rodents (when rodents bite the cables it will cause short circuit). Lead conduits are used in factories or when the building is prone to fire accident. The cables in conduit should not be too tight. Space factor have to be put into consideration.

### Types of Conduit:

Following conduits are used in the conduit wiring systems (both concealed and surface conduit wiring) which are shown in the above figure.

- Metallic Conduit

- Non-metallic conduit

### Metallic Conduit:

Metallic conduits are made of steel which are very strong but costly as well. There are two types of metallic conduits.

- Class A Conduit: Low gauge conduit (Thin layer steel sheet conduit)

- Class B Conduit: High gauge conduit (Thick sheet of steel conduit)

### Non-metallic Conduit:

A solid PVC conduit is used as non-metallic conduit now a day, which is flexible and easy to bend.

### Size of Conduit:

The common conduit pipes are available in different sizes genially, 13, 16.2, 18.75, 20, 25, 37, 50, and 63 mm (diameter) or 1/2, 5/8, 3/4, 1, 1.25, 1.5, and 2 inch in diameter.

Advantage of Conduit Wiring Systems

- It is the safest wiring system (Concealed conduit wring)

- Appearance is very beautiful (in case of concealed conduit wiring)

- No risk of mechanical wear & tear and fire in case of metallic pipes.

- Customization can be easily done according to the future needs.

- There is no risk of damage the cables insulation.

- It is safe from corrosion (in case of PVC conduit) and risk of fire.

- It can be used even in humidity, chemical effect and smoky areas.

- No risk of electric shock (In case of proper earthing and grounding of metallic pipes).

- It is reliable and popular wiring system.

- Sustainable and long-lasting wiring system.

Disadvantages of Conduit Wiring Systems

- It is expensive wiring system (Due to PVC and Metallic pipes, Additional earthing for metallic pipes Tee(s) and elbows etc.

- Very difficult to find the defects in the wiring.

- Installation is not easy and simple.

- Risk of Electric shock (In case of metallic pipes without proper earthing system)

- Very complicated to manage additional connection in the future.

Field of Applications:

- Places where considerable dust is present such as in textile mills, saw mills, flour mills etc.

- Damped situations.

- In workshop for lighting & motor wiring.

- Places where there is possibility of fire hazards such as in oil mills, varnish factories etc.

- Places where important documents are kept such as record room.

- Residential & public building where appearance is the prime thing.